## YTD Metrics report
Unit | Month | MWH | Period Hours | Gross Maximum Capacity MW | Service Hours | Reserve Shutdown Hours | Available Hours | Available MWH | Forced Outage Hours | Planned Outage Hours | Extended Scheduled Outage Hours | Maintenance Outage Hours | Unavailable Hours | Unplanned Outage Hours | Service Factor | Forced Outage Factor | Availability Factor | Gross Capacity Factor | Unplanned Outage Factor | Number of Reserve Shutdowns | Number of Forced Outages | Number of Planned Outages | Number of Planned Outage Extensions |  | Number of Maintenance Outages | Number of Maintenance Outage Extensions
|  |  | PH | GMC | SH | RSH | AH |  | FOH | POH | ESOH | MOH | UH | UOH | SF | FOF | AF | GCF | UOF |  |  |  | Hours | Count |  | Hours | Count
P01 | 2023-01-01 | 48935.7 | 744 | 95 | 705.05 | 23.13 | 728.18 | 69177.1 | 0 | 15.82 | 0 | 0 | 15.82 | 0 | 94.76 | 0 | 97.87 | 69.24 | 0 | 5 | 0 | 2 | 0 | 0 | 0 | 0 | 0
P01 | 2023-02-02 | 43422 | 672 | 95 | 633.75 | 22.4 | 656.15 | 62334.25 | 15.85 | 0 | 0 | 0 | 15.85 | 15.85 | 94.31 | 2.36 | 97.64 | 68.02 | 0.023586 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0
P01 | 2023-03-03 | 45003.8 | 744 | 95 | 687.48 | 56.52 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 92.4 | 0 | 100 | 63.67 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P01 | 2023-04-04 | 50398.5 | 720 | 95 | 718.97 | 1.03 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 99.86 | 0 | 100 | 73.68 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P01 | 2023-05-05 | 53646.3 | 744 | 95 | 744 | 0 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 75.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P01 | 2023-06-06 | 49895.9 | 720 | 95 | 719.18 | 0.82 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 99.89 | 0 | 100 | 72.95 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P01 | 2023-07-07 | 54930.7 | 744 | 95 | 740.48 | 3.52 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 99.53 | 0 | 100 | 77.72 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P01 | 2022-08-08 | 56589.4 | 744 | 95 | 727.68 | 16.32 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 97.81 | 0 | 100 | 80.06 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P01 | 2022-09-09 | 18560.7 | 720 | 95 | 249.23 | 179.72 | 428.95 | 40750.25 | 0 | 291.05 | 0 | 0 | 291.05 | 0 | 34.62 | 0 | 59.58 | 27.14 | 0 | 15 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P01 | 2022-10-10 | 43479.8 | 744 | 95 | 628 | 116 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 84.41 | 0 | 100 | 61.52 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P01 | 2022-11-11 | 42312.9 | 720 | 95 | 553.1 | 156.9 | 710 | 67450 | 0.65 | 9.35 | 0 | 0 | 10 | 0.65 | 76.82 | 0.09 | 98.61 | 61.86 | 0.00090278 | 23 | 1 | 1 | 0 | 0 | 0 | 0 | 0
P01 | 2022-12-12 | 48997 | 744 | 95 | 635.52 | 108.48 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 85.42 | 0 | 100 | 69.32 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P01 | Total | 556172.7 | 8760 | 95 | 7742.44 | 684.84 | 8427.28 | 800591.6 | 16.5 | 316.22 | 0 | 0 | 332.72 | 16.5 | 88.3192 | 0.20417 | 96.1417 | 66.7567 | 0.0020408 | 92 | 2 | 4 | 0 | 0 | 0 | 0 | 0
P02 | 2023-01-01 | 41192.8 | 744 | 95 | 574.22 | 160.78 | 735 | 69825 | 0 | 9 | 0 | 0 | 9 | 0 | 77.18 | 0 | 98.79 | 58.28 | 0 | 24 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P02 | 2023-02-02 | 40486.1 | 672 | 95 | 560.22 | 95.93 | 656.15 | 62334.25 | 15.85 | 0 | 0 | 0 | 15.85 | 15.85 | 83.37 | 2.36 | 97.64 | 63.42 | 0.023586 | 19 | 1 | 0 | 0 | 0 | 0 | 0 | 0
P02 | 2023-03-03 | 38691.1 | 744 | 95 | 552.4 | 191.6 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 74.25 | 0 | 100 | 54.74 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P02 | 2023-04-04 | 21784.7 | 720 | 95 | 280.82 | 429.18 | 710 | 67450 | 0 | 0 | 0 | 10 | 10 | 10 | 39 | 0 | 98.61 | 31.85 | 0.013889 | 3 | 0 | 0 | 0 | 0 | 1 | 0 | 0
P02 | 2023-05-05 | 53506.4 | 744 | 95 | 734.9 | 0.07 | 734.97 | 69822.15 | 0 | 0 | 0 | 9.03 | 9.03 | 9.03 | 98.78 | 0 | 98.79 | 75.7 | 0.012137 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0
P02 | 2023-06-06 | 50126.9 | 720 | 95 | 709.15 | 10.85 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 98.49 | 0 | 100 | 73.29 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P02 | 2023-07-07 | 50332.4 | 744 | 95 | 689.18 | 54.82 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 92.63 | 0 | 100 | 71.21 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P02 | 2022-08-08 | 54370.1 | 744 | 95 | 738.42 | 5.58 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 99.25 | 0 | 100 | 76.92 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P02 | 2022-09-09 | 11831.6 | 720 | 95 | 167.05 | 103.18 | 270.23 | 25671.85 | 0 | 273.77 | 176 | 0 | 449.77 | 0 | 23.2 | 0 | 37.53 | 17.3 | 0 | 13 | 0 | 1 | 176 | 1 | 0 | 0 | 0
P02 | 2022-10-10 | 31249.2 | 744 | 95 | 428.57 | 35.6 | 464.17 | 44096.15 | 0 | 0 | 279.83 | 0 | 279.83 | 0 | 57.6 | 0 | 62.39 | 44.21 | 0 | 6 | 0 | 0 | 279.83 | 1 | 0 | 0 | 0
P02 | 2022-11-11 | 49555.7 | 720 | 95 | 653.8 | 58.57 | 712.37 | 67675.15 | 0.65 | 6.98 | 0 | 0 | 7.63 | 0.65 | 90.81 | 0.09 | 98.94 | 72.45 | 0.00090278 | 9 | 1 | 1 | 0 | 0 | 0 | 0 | 0
P02 | 2022-12-12 | 53736.6 | 744 | 95 | 713.6 | 30.4 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 95.91 | 0 | 100 | 76.03 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P02 | Total | 496863.6 | 8760 | 95 | 6802.33 | 1176.56 | 7978.89 | 757994.55 | 16.5 | 289.75 | 455.83 | 19.03 | 781.11 | 35.53 | 77.5392 | 0.20417 | 91.0575 | 59.6167 | 0.0042096 | 135 | 2 | 3 | 455.83 | 2 | 2 | 0 | 0
P03 | 2023-01-01 | 47565.2 | 744 | 95 | 703.52 | 31.23 | 734.75 | 69801.25 | 0 | 8 | 1.25 | 0 | 9.25 | 0 | 94.56 | 0 | 98.76 | 67.3 | 0 | 6 | 0 | 1 | 1.25 | 1 | 0 | 0 | 0
P03 | 2023-02-02 | 44433.9 | 672 | 95 | 648.87 | 7.28 | 656.15 | 62334.25 | 15.85 | 0 | 0 | 0 | 15.85 | 15.85 | 96.56 | 2.36 | 97.64 | 69.6 | 0.023586 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0
P03 | 2023-03-03 | 39053.3 | 744 | 95 | 600.78 | 137.33 | 738.11 | 70120.45 | 0 | 0.67 | 0 | 5.22 | 5.89 | 5.22 | 80.75 | 0 | 99.21 | 55.25 | 0.0070161 | 7 | 0 | 1 | 0 | 0 | 2 | 0 | 0
P03 | 2023-04-04 | 49130.4 | 720 | 95 | 710.7 | 0 | 710.7 | 67516.5 | 0 | 0 | 0 | 9.3 | 9.3 | 9.3 | 98.71 | 0 | 98.71 | 71.83 | 0.012917 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
P03 | 2023-05-05 | 52749 | 744 | 95 | 737.25 | 1.22 | 738.47 | 70154.65 | 0 | 0 | 0 | 5.53 | 5.53 | 5.53 | 99.09 | 0 | 99.26 | 74.63 | 0.0074328 | 3 | 0 | 0 | 0 | 0 | 2 | 0 | 0
P03 | 2023-06-06 | 49500.4 | 720 | 95 | 719.4 | 0.6 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 99.92 | 0 | 100 | 72.37 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P03 | 2023-07-07 | 53064.1 | 744 | 95 | 744 | 0 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 75.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P03 | 2022-08-08 | 52986.9 | 744 | 95 | 740.13 | 3.87 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 99.48 | 0 | 100 | 74.97 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P03 | 2022-09-09 | 39519 | 720 | 95 | 578.36 | 60.07 | 638.43 | 60650.85 | 0 | 81.57 | 0 | 0 | 81.57 | 0 | 80.33 | 0 | 88.67 | 57.78 | 0 | 13 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P03 | 2022-10-10 | 48169.2 | 744 | 95 | 699.12 | 44.88 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 93.97 | 0 | 100 | 68.15 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P03 | 2022-11-11 | 46233.6 | 720 | 95 | 626.6 | 92.75 | 719.35 | 68338.25 | 0.65 | 0 | 0 | 0 | 0.65 | 0.65 | 87.03 | 0.09 | 99.91 | 67.59 | 0.00090278 | 18 | 1 | 0 | 0 | 0 | 0 | 0 | 0
P03 | 2022-12-12 | 52313.6 | 744 | 95 | 727.43 | 16.57 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 97.77 | 0 | 100 | 74.02 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P03 | Total | 574718.6 | 8760 | 95 | 8236.16 | 395.8 | 8631.96 | 820036.2 | 16.5 | 90.24 | 1.25 | 20.05 | 128.04 | 36.55 | 94.0142 | 0.20417 | 98.5133 | 69.0475 | 0.0043212 | 66 | 2 | 3 | 1.25 | 1 | 5 | 0 | 0
P04 | 2023-01-01 | 41400.1 | 744 | 95 | 577.18 | 166.82 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 77.58 | 0 | 100 | 58.57 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P04 | 2023-02-02 | 36753.8 | 672 | 95 | 509.12 | 147.03 | 656.15 | 62334.25 | 15.85 | 0 | 0 | 0 | 15.85 | 15.85 | 75.76 | 2.36 | 97.64 | 57.57 | 0.023586 | 22 | 1 | 0 | 0 | 0 | 0 | 0 | 0
P04 | 2023-03-03 | 24346.3 | 744 | 95 | 320.71 | 356.22 | 676.93 | 64308.35 | 0 | 67.07 | 0 | 0 | 67.07 | 0 | 43.11 | 0 | 90.99 | 34.45 | 0 | 22 | 0 | 3 | 0 | 0 | 0 | 0 | 0
P04 | 2023-04-04 | 4040.5 | 720 | 95 | 55.75 | 664.25 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 7.74 | 0 | 100 | 5.91 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P04 | 2023-05-05 | 54247.5 | 744 | 95 | 744 | 0 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 76.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P04 | 2023-06-06 | 49066.8 | 720 | 95 | 694.67 | 25.33 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 96.48 | 0 | 100 | 71.74 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P04 | 2023-07-07 | 46460.8 | 744 | 95 | 637.42 | 106.58 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 85.67 | 0 | 100 | 65.73 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P04 | 2022-08-08 | 0 | 744 | 95 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 0 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P04 | 2022-09-09 | 31784 | 720 | 95 | 439.73 | 141.67 | 581.4 | 55233 | 0 | 121.22 | 0 | 17.38 | 138.6 | 17.38 | 61.07 | 0 | 80.75 | 46.47 | 0.024139 | 37 | 0 | 2 | 0 | 0 | 4 | 0 | 0
P04 | 2022-10-10 | 41656.7 | 744 | 95 | 573.98 | 170.02 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 77.15 | 0 | 100 | 58.94 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P04 | 2022-11-11 | 45769.3 | 720 | 95 | 600.59 | 112.92 | 713.51 | 67783.45 | 0.62 | 0 | 0 | 5.87 | 6.49 | 6.49 | 83.42 | 0.09 | 99.1 | 66.91 | 0.0090139 | 28 | 1 | 0 | 0 | 0 | 1 | 0 | 0
P04 | 2022-12-12 | 45286.5 | 744 | 95 | 590.85 | 153.15 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 79.42 | 0 | 100 | 64.07 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P04 | Total | 420812.3 | 8760 | 95 | 5744 | 2043.99 | 7787.99 | 739859.05 | 16.47 | 932.29 | 0 | 23.25 | 972.01 | 39.72 | 65.6167 | 0.20417 | 89.04 | 50.5925 | 0.0047283 | 218 | 2 | 6 | 0 | 0 | 5 | 0 | 0
P05 | 2023-01-01 | 45391.6 | 744 | 95 | 666.26 | 70.07 | 736.33 | 69951.35 | 0 | 7.67 | 0 | 0 | 7.67 | 0 | 89.55 | 0 | 98.97 | 64.22 | 0 | 8 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P05 | 2023-02-02 | 44976.3 | 672 | 95 | 635.53 | 36.47 | 672 | 63840 | 0 | 0 | 0 | 0 | 0 | 0 | 94.57 | 0 | 100 | 70.45 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P05 | 2023-03-03 | 41391.3 | 744 | 95 | 629.48 | 114.52 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 84.61 | 0 | 100 | 58.56 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P05 | 2023-04-04 | 30372.2 | 720 | 95 | 464.9 | 255.1 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 64.57 | 0 | 100 | 44.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P05 | 2023-05-05 | 54770.6 | 744 | 95 | 739.42 | 4.58 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 99.38 | 0 | 100 | 77.49 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P05 | 2023-06-06 | 45688.6 | 720 | 95 | 656.6 | 63.4 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 91.19 | 0 | 100 | 66.8 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P05 | 2023-07-07 | 34521.4 | 744 | 95 | 478.33 | 265.67 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 64.29 | 0 | 100 | 48.84 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P05 | 2022-08-08 | 52760 | 744 | 95 | 734.92 | 9.08 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 98.78 | 0 | 100 | 74.65 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P05 | 2022-09-09 | 43784.5 | 720 | 95 | 628.48 | 91.52 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 87.29 | 0 | 100 | 64.01 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P05 | 2022-10-10 | 17958.4 | 744 | 95 | 264.18 | 126.2 | 390.38 | 37086.1 | 0 | 353.62 | 0 | 0 | 353.62 | 0 | 35.51 | 0 | 52.47 | 25.41 | 0 | 10 | 0 | 2 | 0 | 0 | 0 | 0 | 0
P05 | 2022-11-11 | 49874.2 | 720 | 95 | 670.05 | 45.83 | 715.88 | 68008.6 | 0 | 0 | 0 | 4.12 | 4.12 | 4.12 | 93.06 | 0 | 99.43 | 72.92 | 0.0057222 | 8 | 0 | 0 | 0 | 0 | 1 | 0 | 0
P05 | 2022-12-12 | 52562.6 | 744 | 95 | 726.9 | 17.1 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 97.7 | 0 | 100 | 74.37 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P05 | Total | 514051.7 | 8760 | 95 | 7295.05 | 1099.54 | 8394.59 | 797486.05 | 0 | 361.29 | 0 | 4.12 | 365.41 | 4.12 | 83.375 | 0 | 95.9058 | 61.8433 | 0.00047685 | 108 | 0 | 3 | 0 | 0 | 1 | 0 | 0
P06 | 2023-01-01 | 43469 | 744 | 95 | 641.82 | 95.68 | 737.5 | 70062.5 | 0 | 6 | 0.5 | 0 | 6.5 | 0 | 86.27 | 0 | 99.13 | 61.5 | 0 | 8 | 0 | 1 | 0.5 | 1 | 0 | 0 | 0
P06 | 2023-02-02 | 42422.7 | 672 | 95 | 611.02 | 60.98 | 672 | 63840 | 0 | 0 | 0 | 0 | 0 | 0 | 90.93 | 0 | 100 | 66.45 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P06 | 2023-03-03 | 23512.1 | 744 | 95 | 359.63 | 384.37 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 48.34 | 0 | 100 | 33.27 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P06 | 2023-04-04 | 12521.6 | 720 | 95 | 209.91 | 502.17 | 712.08 | 67647.6 | 0 | 0 | 0 | 7.92 | 7.92 | 7.92 | 29.15 | 0 | 98.9 | 18.31 | 0.011 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0
P06 | 2023-05-05 | 49898.4 | 744 | 95 | 698.12 | 45.88 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 93.83 | 0 | 100 | 70.6 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P06 | 2023-06-06 | 42582.5 | 720 | 95 | 618.35 | 101.65 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 85.88 | 0 | 100 | 62.26 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P06 | 2023-07-07 | 52135 | 744 | 95 | 729.1 | 14.9 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 100 | 73.76 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P06 | 2022-08-08 | 52640.3 | 744 | 95 | 733.95 | 10.05 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 98.65 | 0 | 100 | 74.48 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P06 | 2022-09-09 | 44519.8 | 720 | 95 | 641.18 | 78.82 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 89.05 | 0 | 100 | 65.09 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P06 | 2022-10-10 | 6022.1 | 744 | 95 | 86.91 | 194.22 | 281.13 | 26707.35 | 0 | 442 | 20.87 | 0 | 462.87 | 0 | 11.68 | 0 | 37.79 | 8.52 | 0 | 10 | 0 | 1 | 20.87 | 1 | 0 | 0 | 0
P06 | 2022-11-11 | 34384.5 | 720 | 95 | 464.6 | 237.78 | 702.38 | 66726.1 | 17.62 | 0 | 0 | 0 | 17.62 | 17.62 | 64.53 | 2.45 | 97.55 | 50.27 | 0.024472 | 27 | 1 | 0 | 0 | 0 | 0 | 0 | 0
P06 | 2022-12-12 | 49882.3 | 744 | 95 | 692.03 | 51.97 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 93.01 | 0 | 100 | 70.57 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P06 | Total | 453990.3 | 8760 | 95 | 6486.62 | 1778.47 | 8265.09 | 785183.55 | 17.62 | 448 | 21.37 | 7.92 | 494.91 | 25.54 | 74.11 | 0.20417 | 94.4475 | 54.59 | 0.002956 | 125 | 1 | 2 | 21.37 | 2 | 1 | 0 | 0
P07 | 2023-01-01 | 0 | 744 | 95 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 0 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P07 | 2023-02-02 | 0 | 672 | 95 | 0 | 0 | 0 | 0 | 0 | 672 | 0 | 0 | 672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P07 | 2023-03-03 | 0 | 744 | 95 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 0 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P07 | 2023-04-04 | 0 | 720 | 95 | 0 | 0 | 0 | 0 | 0 | 720 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P07 | 2023-05-05 | 0 | 744 | 95 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 0 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P07 | 2023-06-06 | 0 | 720 | 95 | 0 | 0 | 0 | 0 | 0 | 720 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P07 | 2023-07-07 | 0 | 744 | 95 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 0 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P07 | 2022-08-08 | 51992.1 | 744 | 95 | 724.48 | 19.52 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 97.38 | 0 | 100 | 73.56 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P07 | 2022-09-09 | 25423 | 720 | 95 | 379.37 | 58.9 | 438.27 | 41635.65 | 0 | 281.73 | 0 | 0 | 281.73 | 0 | 52.69 | 0 | 60.87 | 37.17 | 0 | 11 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P07 | 2022-10-10 | 0 | 744 | 95 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 0 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P07 | 2022-11-11 | 0 | 720 | 95 | 0 | 0 | 0 | 0 | 0 | 720 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P07 | 2022-12-12 | 0 | 744 | 95 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 0 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P07 | Total | 77415.1 | 8760 | 95 | 1103.85 | 78.42 | 1182.27 | 112315.65 | 0 | 7577.73 | 0 | 0 | 7577.73 | 0 | 12.5058 | 0 | 13.4058 | 9.2275 | 0 | 21 | 0 | 11 | 0 | 0 | 0 | 0 | 0
P08 | 2023-01-01 | 35876.9 | 744 | 95 | 501.48 | 242.52 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 67.4 | 0 | 100 | 50.76 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P08 | 2023-02-02 | 34744.4 | 672 | 95 | 474.22 | 197.78 | 672 | 63840 | 0 | 0 | 0 | 0 | 0 | 0 | 70.57 | 0 | 100 | 54.42 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P08 | 2023-03-03 | 33135.8 | 744 | 95 | 470.28 | 269.6 | 739.88 | 70288.6 | 0 | 4.12 | 0 | 0 | 4.12 | 0 | 63.21 | 0 | 99.45 | 46.88 | 0 | 18 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P08 | 2023-04-04 | 0 | 720 | 95 | 0 | 720 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P08 | 2023-05-05 | 48466.4 | 744 | 95 | 667.32 | 76.68 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 89.69 | 0 | 100 | 68.57 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P08 | 2023-06-06 | 29119 | 720 | 95 | 414.9 | 305.1 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 57.63 | 0 | 100 | 42.57 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P08 | 2023-07-07 | 23533.1 | 744 | 95 | 320.32 | 423.68 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 43.05 | 0 | 100 | 33.3 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P08 | 2022-08-08 | 50266.1 | 744 | 95 | 681.32 | 62.68 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 91.58 | 0 | 100 | 71.12 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P08 | 2022-09-09 | 28391.5 | 720 | 95 | 385.72 | 334.28 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 53.57 | 0 | 100 | 41.51 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P08 | 2022-10-10 | 11075.8 | 744 | 95 | 151 | 324.73 | 475.73 | 45194.35 | 0 | 268 | 0.27 | 0 | 268.27 | 0 | 20.3 | 0 | 63.94 | 15.67 | 0 | 23 | 0 | 2 | 0.27 | 1 | 0 | 0 | 0
P08 | 2022-11-11 | 0 | 720 | 95 | 0 | 0 | 0 | 0 | 0 | 720 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P08 | 2022-12-12 | 24376.5 | 744 | 95 | 330.25 | 53.23 | 383.48 | 36430.6 | 0 | 351.1 | 0 | 9.42 | 360.52 | 9.42 | 44.39 | 0 | 51.54 | 34.49 | 0.012661 | 9 | 0 | 1 | 0 | 0 | 1 | 0 | 0
P08 | Total | 318985.5 | 8760 | 95 | 4396.81 | 3010.28 | 7407.09 | 703673.55 | 0 | 1343.22 | 0.27 | 9.42 | 1352.91 | 9.42 | 50.1158 | 0 | 84.5775 | 38.2742 | 0.0010551 | 206 | 0 | 5 | 0.27 | 1 | 1 | 0 | 0
P09 | 2023-01-01 | 32569.3 | 744 | 95 | 457.83 | 286.17 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 61.54 | 0 | 100 | 46.08 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P09 | 2023-02-02 | 28159.8 | 672 | 95 | 385.74 | 282.08 | 667.82 | 63442.9 | 0 | 4.18 | 0 | 0 | 4.18 | 0 | 57.4 | 0 | 99.38 | 44.11 | 0 | 40 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P09 | 2023-03-03 | 13456.8 | 744 | 95 | 194.02 | 497.28 | 691.3 | 65673.5 | 0 | 52.7 | 0 | 0 | 52.7 | 0 | 26.08 | 0 | 92.92 | 19.04 | 0 | 15 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P09 | 2023-04-04 | 31053.8 | 720 | 95 | 453.55 | 256.17 | 709.72 | 67423.4 | 0 | 0 | 0.28 | 10 | 10.28 | 10 | 62.99 | 0 | 98.57 | 45.4 | 0.013889 | 3 | 0 | 0 | 0 | 0 | 1 | 0.28 | 1
P09 | 2023-05-05 | 41843.7 | 744 | 95 | 581.9 | 162.1 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 78.21 | 0 | 100 | 59.2 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P09 | 2023-06-06 | 9820.4 | 720 | 95 | 143.86 | 572.42 | 716.28 | 68046.6 | 3.72 | 0 | 0 | 0 | 3.72 | 3.72 | 19.98 | 0.52 | 99.48 | 14.36 | 0.0051667 | 16 | 1 | 0 | 0 | 0 | 0 | 0 | 0
P09 | 2023-07-07 | 6123.5 | 744 | 95 | 87.35 | 656.65 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 11.74 | 0 | 100 | 8.66 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P09 | 2022-08-08 | 44655.5 | 744 | 95 | 611.03 | 132.97 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 82.13 | 0 | 100 | 63.18 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P09 | 2022-09-09 | 24116.3 | 720 | 95 | 335.88 | 305.97 | 641.85 | 60975.75 | 0 | 78.15 | 0 | 0 | 78.15 | 0 | 46.65 | 0 | 89.15 | 35.26 | 0 | 32 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P09 | 2022-10-10 | 18826.8 | 744 | 95 | 255.5 | 488.5 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 34.34 | 0 | 100 | 26.64 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P09 | 2022-11-11 | 28193.8 | 720 | 95 | 366.07 | 345.28 | 711.35 | 67578.25 | 0 | 8.65 | 0 | 0 | 8.65 | 0 | 50.84 | 0 | 98.8 | 41.22 | 0 | 37 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P09 | 2022-12-12 | 37827.4 | 744 | 95 | 495.6 | 241.05 | 736.65 | 69981.75 | 0 | 0 | 0 | 7.35 | 7.35 | 7.35 | 66.61 | 0 | 99.01 | 53.52 | 0.009879 | 24 | 0 | 0 | 0 | 0 | 2 | 0 | 0
P09 | Total | 316647.1 | 8760 | 95 | 4368.33 | 4226.64 | 8594.97 | 816522.15 | 3.72 | 143.68 | 0.28 | 17.35 | 165.03 | 21.07 | 49.8758 | 0.043333 | 98.1092 | 38.0558 | 0.0024112 | 292 | 1 | 4 | 0 | 0 | 3 | 0.28 | 1
P10 | 2023-01-01 | 40350.6 | 744 | 95 | 590.93 | 153.07 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 79.43 | 0 | 100 | 57.09 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P10 | 2023-02-02 | 38473.6 | 672 | 95 | 548.5 | 119.32 | 667.82 | 63442.9 | 0 | 4.18 | 0 | 0 | 4.18 | 0 | 81.62 | 0 | 99.38 | 60.27 | 0 | 18 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P10 | 2023-03-03 | 35204.5 | 744 | 95 | 535.9 | 154.73 | 690.63 | 65609.85 | 0 | 53.37 | 0 | 0 | 53.37 | 0 | 72.03 | 0 | 92.83 | 49.81 | 0 | 16 | 0 | 2 | 0 | 0 | 0 | 0 | 0
P10 | 2023-04-04 | 29089.7 | 720 | 95 | 445.67 | 274.33 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9 | 0 | 100 | 42.53 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P10 | 2023-05-05 | 33981.8 | 744 | 95 | 469.25 | 274.75 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 63.07 | 0 | 100 | 48.08 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P10 | 2023-06-06 | 1111.3 | 720 | 95 | 17.02 | 702.98 | 720 | 68400 | 0 | 0 | 0 | 0 | 0 | 0 | 2.36 | 0 | 100 | 1.62 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P10 | 2023-07-07 | 1921.1 | 744 | 95 | 28.52 | 715.48 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 3.83 | 0 | 100 | 2.72 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P10 | 2022-08-08 | 36828.3 | 744 | 95 | 506.23 | 237.77 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 68.04 | 0 | 100 | 52.11 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P10 | 2022-09-09 | 34010.2 | 720 | 95 | 491.35 | 150.57 | 641.92 | 60982.4 | 0 | 78.08 | 0 | 0 | 78.08 | 0 | 68.24 | 0 | 89.16 | 49.72 | 0 | 22 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P10 | 2022-10-10 | 33131.1 | 744 | 95 | 483.45 | 260.55 | 744 | 70680 | 0 | 0 | 0 | 0 | 0 | 0 | 64.98 | 0 | 100 | 46.87 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P10 | 2022-11-11 | 40301.2 | 720 | 95 | 545.27 | 166.08 | 711.35 | 67578.25 | 0 | 8.65 | 0 | 0 | 8.65 | 0 | 75.73 | 0 | 98.8 | 58.92 | 0 | 24 | 0 | 1 | 0 | 0 | 0 | 0 | 0
P10 | 2022-12-12 | 46065.9 | 744 | 95 | 632.27 | 104.35 | 736.62 | 69978.9 | 0 | 0 | 0 | 7.38 | 7.38 | 7.38 | 84.98 | 0 | 99.01 | 65.18 | 0.0099194 | 15 | 0 | 0 | 0 | 0 | 2 | 0 | 0
P10 | Total | 370469.3 | 8760 | 95 | 5294.36 | 3313.98 | 8608.34 | 817792.3 | 0 | 144.28 | 0 | 7.38 | 151.66 | 7.38 | 60.5175 | 0 | 98.265 | 44.5767 | 0.00082661 | 190 | 0 | 5 | 0 | 0 | 2 | 0 | 0
PR | TOTAL | 4100126.2 | 87600 |  | 57469.95 | 17808.52 | 75278.47 | 7151454.65 | 87.31 | 11646.7 | 479 | 108.52 | 12321.53 | 195.83 | 65.5989 | 0.10642 | 85.9463 | 49.2581 | 0.0023026 | 1453 | 10 | 46 | 478.72 | 6 | 20 | 0.28 | 1
W01 | 2023-01-01 | 35910.7 | 744 | 122 | 485.22 | 36.83 | 522.05 | 63690.1 | 0 | 221.95 | 0 | 0 | 221.95 | 0 | 65.22 | 0 | 70.17 | 39.56 | 0 | 12 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W01 | 2023-02-02 | 45833.6 | 672 | 122 | 616.55 | 55.45 | 672 | 81984 | 0 | 0 | 0 | 0 | 0 | 0 | 91.75 | 0 | 100 | 55.91 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W01 | 2023-03-03 | 34847.1 | 744 | 122 | 481.35 | 262.65 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 64.7 | 0 | 100 | 38.39 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W01 | 2023-04-04 | 10198 | 720 | 122 | 148.23 | 571.77 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 20.59 | 0 | 100 | 11.61 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W01 | 2023-05-05 | 40569.9 | 744 | 122 | 517.3 | 226.43 | 743.73 | 90735.06 | 0 | 0 | 0 | 0.27 | 0.27 | 0.27 | 69.53 | 0 | 99.96 | 44.7 | 0.0003629 | 27 | 0 | 0 | 0 | 0 | 2 | 0 | 0
W01 | 2023-06-06 | 3470.8 | 720 | 122 | 47.72 | 666.03 | 713.75 | 87077.5 | 6.25 | 0 | 0 | 0 | 6.25 | 6.25 | 6.63 | 0.87 | 99.13 | 3.95 | 0.0086806 | 18 | 1 | 0 | 0 | 0 | 0 | 0 | 0
W01 | 2023-07-07 | 7027.5 | 744 | 122 | 96.32 | 647.68 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 12.95 | 0 | 100 | 7.74 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W01 | 2022-08-08 | 33532.9 | 744 | 122 | 433.1 | 310.9 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 58.21 | 0 | 100 | 36.94 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W01 | 2022-09-09 | 39229.6 | 720 | 122 | 550.47 | 169.53 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 76.45 | 0 | 100 | 44.66 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W01 | 2022-10-10 | 22228.3 | 744 | 122 | 314.53 | 351.52 | 666.05 | 81258.1 | 0 | 77.95 | 0 | 0 | 77.95 | 0 | 42.28 | 0 | 89.52 | 24.49 | 0 | 35 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W01 | 2022-11-11 | 44856.8 | 720 | 122 | 584.78 | 135.22 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 81.22 | 0 | 100 | 51.07 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W01 | 2022-12-12 | 44528.7 | 744 | 122 | 623.7 | 120.3 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 83.83 | 0 | 100 | 49.06 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W01 | Total | 362233.9 | 8760 | 122 | 4899.27 | 3554.31 | 8453.58 | 1031336.76 | 6.25 | 299.9 | 0 | 0.27 | 306.42 | 6.52 | 56.1133 | 0.0725 | 96.565 | 34.0067 | 0.00075362 | 336 | 1 | 2 | 0 | 0 | 2 | 0 | 0
W02 | 2023-01-01 | 3545.7 | 744 | 122 | 49.97 | 4.03 | 54 | 6588 | 0 | 690 | 0 | 0 | 690 | 0 | 6.72 | 0 | 7.26 | 3.91 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W02 | 2023-02-02 | 0 | 672 | 122 | 0 | 0 | 0 | 0 | 0 | 672 | 0 | 0 | 672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W02 | 2023-03-03 | 11489.6 | 744 | 122 | 164.37 | 14 | 178.37 | 21761.14 | 0 | 565.63 | 0 | 0 | 565.63 | 0 | 22.09 | 0 | 23.97 | 12.66 | 0 | 4 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W02 | 2023-04-04 | 30116 | 720 | 122 | 432.88 | 287.12 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 60.12 | 0 | 100 | 34.29 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W02 | 2023-05-05 | 48698 | 744 | 122 | 623.68 | 114.7 | 738.38 | 90082.36 | 0 | 0 | 0 | 5.62 | 5.62 | 5.62 | 83.83 | 0 | 99.24 | 53.65 | 0.0075538 | 17 | 0 | 0 | 0 | 0 | 1 | 0 | 0
W02 | 2023-06-06 | 9766.9 | 720 | 122 | 135.32 | 584.68 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 18.79 | 0 | 100 | 11.12 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W02 | 2023-07-07 | 11704.2 | 744 | 122 | 160.1 | 583.9 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 21.52 | 0 | 100 | 12.89 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W02 | 2022-08-08 | 45710.3 | 744 | 122 | 588.42 | 155.58 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 79.09 | 0 | 100 | 50.36 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W02 | 2022-09-09 | 51301.9 | 720 | 122 | 720 | 0 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 58.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W02 | 2022-10-10 | 46163 | 744 | 122 | 653.78 | 9.95 | 663.73 | 80975.06 | 0 | 80.27 | 0 | 0 | 80.27 | 0 | 87.87 | 0 | 89.21 | 50.86 | 0 | 4 | 0 | 2 | 0 | 0 | 0 | 0 | 0
W02 | 2022-11-11 | 54703.1 | 720 | 122 | 718.43 | 1.57 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 99.78 | 0 | 100 | 62.28 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W02 | 2022-12-12 | 52831.6 | 744 | 122 | 738.82 | 5.18 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 99.3 | 0 | 100 | 58.21 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W02 | Total | 366030.3 | 8760 | 122 | 4985.77 | 1760.71 | 6746.48 | 823070.56 | 0 | 2007.9 | 0 | 5.62 | 2013.52 | 5.62 | 56.5925 | 0 | 76.64 | 34.0525 | 0.00062948 | 142 | 0 | 5 | 0 | 0 | 1 | 0 | 0
W03 | 2023-01-01 | 51999.6 | 744 | 122 | 699.95 | 44.05 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 94.08 | 0 | 100 | 57.29 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W03 | 2023-02-02 | 43672.3 | 672 | 122 | 583.42 | 88.58 | 672 | 81984 | 0 | 0 | 0 | 0 | 0 | 0 | 86.82 | 0 | 100 | 53.27 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W03 | 2023-03-03 | 29164.9 | 744 | 122 | 402.3 | 337.72 | 740.02 | 90282.44 | 0 | 0 | 0 | 3.98 | 3.98 | 3.98 | 54.07 | 0 | 99.47 | 32.13 | 0.0053495 | 58 | 0 | 0 | 0 | 0 | 1 | 0 | 0
W03 | 2023-04-04 | 7114.4 | 720 | 122 | 102.3 | 617.7 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 14.21 | 0 | 100 | 8.1 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W03 | 2023-05-05 | 48714.6 | 744 | 122 | 623.37 | 120.63 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 83.79 | 0 | 100 | 53.67 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W03 | 2023-06-06 | 19783.9 | 720 | 122 | 269.02 | 450.98 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 37.36 | 0 | 100 | 22.52 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W03 | 2023-07-07 | 20217.7 | 744 | 122 | 276.65 | 467.35 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 37.18 | 0 | 100 | 22.27 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W03 | 2022-08-08 | 53062.5 | 744 | 122 | 675.37 | 68.35 | 743.72 | 90733.84 | 0 | 0 | 0 | 0.28 | 0.28 | 0.28 | 90.78 | 0 | 99.96 | 58.46 | 0.00037634 | 24 | 0 | 0 | 0 | 0 | 1 | 0 | 0
W03 | 2022-09-09 | 40430.5 | 720 | 122 | 565.05 | 154.95 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 78.48 | 0 | 100 | 46.03 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W03 | 2022-10-10 | 33356.6 | 744 | 122 | 467.65 | 196.97 | 664.62 | 81083.64 | 47.85 | 31.53 | 0 | 0 | 79.38 | 47.85 | 62.86 | 6.43 | 89.33 | 36.75 | 0.064315 | 35 | 1 | 1 | 0 | 0 | 0 | 0 | 0
W03 | 2022-11-11 | 52464 | 720 | 122 | 688.97 | 31.03 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 95.69 | 0 | 100 | 59.73 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W03 | 2022-12-12 | 47267.1 | 744 | 122 | 660.95 | 83.05 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 88.84 | 0 | 100 | 52.07 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W03 | Total | 447248.1 | 8760 | 122 | 6015 | 2661.36 | 8676.36 | 1058515.92 | 47.85 | 31.53 | 0 | 4.26 | 83.64 | 52.11 | 68.68 | 0.53583 | 99.0633 | 41.8575 | 0.0058367 | 326 | 1 | 1 | 0 | 0 | 2 | 0 | 0
W04 | 2023-01-01 | 32362.8 | 744 | 122 | 435.9 | 308.1 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 58.59 | 0 | 100 | 35.65 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W04 | 2023-02-02 | 31996.9 | 672 | 122 | 428.72 | 243.28 | 672 | 81984 | 0 | 0 | 0 | 0 | 0 | 0 | 63.8 | 0 | 100 | 39.03 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W04 | 2023-03-03 | 23634.8 | 744 | 122 | 327.95 | 416.05 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 44.08 | 0 | 100 | 26.04 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W04 | 2023-04-04 | 13753.6 | 720 | 122 | 198.91 | 440.97 | 639.88 | 78065.36 | 0 | 80.12 | 0 | 0 | 80.12 | 0 | 27.63 | 0 | 88.87 | 15.66 | 0 | 11 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W04 | 2023-05-05 | 51848.2 | 744 | 122 | 673.68 | 70.32 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 90.55 | 0 | 100 | 57.12 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W04 | 2023-06-06 | 29408.3 | 720 | 122 | 403.28 | 316.72 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 56.01 | 0 | 100 | 33.48 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W04 | 2023-07-07 | 28603.9 | 744 | 122 | 394.08 | 349.92 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 52.97 | 0 | 100 | 31.51 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W04 | 2022-08-08 | 50414.7 | 744 | 122 | 643.97 | 100.03 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 86.56 | 0 | 100 | 55.54 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W04 | 2022-09-09 | 12926.9 | 720 | 122 | 178.7 | 541.3 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 24.82 | 0 | 100 | 14.72 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W04 | 2022-10-10 | 12664.8 | 744 | 122 | 177.54 | 534.93 | 712.47 | 86921.34 | 0 | 31.53 | 0 | 0 | 31.53 | 0 | 23.86 | 0 | 95.76 | 13.95 | 0 | 22 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W04 | 2022-11-11 | 29806.2 | 720 | 122 | 378.08 | 310.47 | 688.55 | 84003.1 | 0 | 31.45 | 0 | 0 | 31.45 | 0 | 52.51 | 0 | 95.63 | 33.93 | 0 | 31 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W04 | 2022-12-12 | 31192.7 | 744 | 122 | 439.12 | 304.88 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 59.02 | 0 | 100 | 34.37 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W04 | Total | 348613.8 | 8760 | 122 | 4679.93 | 3936.97 | 8616.9 | 1051261.8 | 0 | 143.1 | 0 | 0 | 143.1 | 0 | 53.3667 | 0 | 98.355 | 32.5833 | 0 | 390 | 0 | 3 | 0 | 0 | 0 | 0 | 0
W05 | 2023-01-01 | 25519.2 | 744 | 122 | 344.77 | 399.23 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 46.34 | 0 | 100 | 28.11 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W05 | 2023-02-02 | 21936.3 | 672 | 122 | 292.47 | 379.53 | 672 | 81984 | 0 | 0 | 0 | 0 | 0 | 0 | 43.52 | 0 | 100 | 26.76 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W05 | 2023-03-03 | 10453.4 | 744 | 122 | 137.53 | 606.47 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 18.49 | 0 | 100 | 11.52 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W05 | 2023-04-04 | 1359 | 720 | 122 | 20.2 | 695.55 | 715.75 | 87321.5 | 0 | 0 | 0.25 | 4 | 4.25 | 4 | 2.81 | 0 | 99.41 | 1.55 | 0.0055556 | 5 | 0 | 0 | 0 | 0 | 1 | 0.25 | 1
W05 | 2023-05-05 | 54357 | 744 | 122 | 711.67 | 32.33 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 95.65 | 0 | 100 | 59.89 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W05 | 2023-06-06 | 36433.7 | 720 | 122 | 500.18 | 219.82 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 69.47 | 0 | 100 | 41.48 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W05 | 2023-07-07 | 36487 | 744 | 122 | 502.55 | 241.45 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 67.55 | 0 | 100 | 40.2 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W05 | 2022-08-08 | 53026.4 | 744 | 122 | 681.87 | 62.13 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 91.65 | 0 | 100 | 58.42 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W05 | 2022-09-09 | 15488 | 720 | 122 | 221.4 | 247.45 | 468.85 | 57199.7 | 0 | 250 | 1.15 | 0 | 251.15 | 0 | 30.75 | 0 | 65.12 | 17.63 | 0 | 10 | 0 | 1 | 1.15 | 1 | 0 | 0 | 0
W05 | 2022-10-10 | 7567.2 | 744 | 122 | 104.78 | 639.22 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 14.08 | 0 | 100 | 8.34 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W05 | 2022-11-11 | 26309.7 | 720 | 122 | 333.32 | 376.38 | 709.7 | 86583.4 | 0 | 10.3 | 0 | 0 | 10.3 | 0 | 46.29 | 0 | 98.57 | 29.95 | 0 | 29 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W05 | 2022-12-12 | 24839.7 | 744 | 122 | 352.85 | 391.15 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 47.43 | 0 | 100 | 27.37 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W05 | Total | 313776.6 | 8760 | 122 | 4203.59 | 4290.71 | 8494.3 | 1036304.6 | 0 | 260.3 | 1.4 | 4 | 265.7 | 4 | 47.8358 | 0 | 96.925 | 29.2683 | 0.00046296 | 334 | 0 | 2 | 1.15 | 1 | 1 | 0.25 | 1
W06 | 2023-01-01 | 53363.4 | 744 | 122 | 736.57 | 7.43 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 100 | 58.79 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W06 | 2023-02-02 | 48127.4 | 672 | 122 | 659.67 | 12.33 | 672 | 81984 | 0 | 0 | 0 | 0 | 0 | 0 | 98.17 | 0 | 100 | 58.7 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W06 | 2023-03-03 | 43840.8 | 744 | 122 | 622.62 | 121.38 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 83.69 | 0 | 100 | 48.3 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W06 | 2023-04-04 | 30035.8 | 720 | 122 | 439.88 | 280.12 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 61.09 | 0 | 100 | 34.19 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W06 | 2023-05-05 | 56007.8 | 744 | 122 | 731.62 | 12.38 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 98.34 | 0 | 100 | 61.7 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W06 | 2023-06-06 | 43494.7 | 720 | 122 | 594.45 | 125.55 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 82.56 | 0 | 100 | 49.52 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W06 | 2023-07-07 | 44156.9 | 744 | 122 | 605.58 | 138.42 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4 | 0 | 100 | 48.65 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W06 | 2022-08-08 | 52192.1 | 744 | 122 | 671.1 | 6.9 | 678 | 82716 | 0 | 66 | 0 | 0 | 66 | 0 | 90.2 | 0 | 91.13 | 57.5 | 0 | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W06 | 2022-09-09 | 0 | 720 | 122 | 0 | 0 | 0 | 0 | 0 | 720 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W06 | 2022-10-10 | 0 | 744 | 122 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 0 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W06 | 2022-11-11 | 16231.8 | 720 | 122 | 223.91 | 0.02 | 223.93 | 27319.46 | 0 | 496.07 | 0 | 0 | 496.07 | 0 | 31.1 | 0 | 31.1 | 18.48 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W06 | 2022-12-12 | 50834.1 | 744 | 122 | 725.99 | 12.08 | 738.07 | 90044.54 | 0 | 0 | 0 | 5.93 | 5.93 | 5.93 | 97.58 | 0 | 99.2 | 56 | 0.0079704 | 9 | 0 | 0 | 0 | 0 | 1 | 0 | 0
W06 | Total | 438284.8 | 8760 | 122 | 6011.39 | 716.61 | 6728 | 820816 | 0 | 2026.07 | 0 | 5.93 | 2032 | 5.93 | 68.5942 | 0 | 76.7858 | 40.9858 | 0.0006642 | 186 | 0 | 4 | 0 | 0 | 1 | 0 | 0
W07 | 2023-01-01 | 44112.4 | 744 | 122 | 599.33 | 144.67 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 80.56 | 0 | 100 | 48.6 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W07 | 2023-02-02 | 40407.2 | 672 | 122 | 544.85 | 127.15 | 672 | 81984 | 0 | 0 | 0 | 0 | 0 | 0 | 81.08 | 0 | 100 | 49.29 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W07 | 2023-03-03 | 23772.6 | 744 | 122 | 325.85 | 408.27 | 734.12 | 89562.64 | 0 | 0 | 0 | 9.88 | 9.88 | 9.88 | 43.8 | 0 | 98.67 | 26.19 | 0.01328 | 54 | 0 | 0 | 0 | 0 | 1 | 0 | 0
W07 | 2023-04-04 | 18111.9 | 720 | 122 | 253.5 | 466.5 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 35.21 | 0 | 100 | 20.62 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W07 | 2023-05-05 | 56910.5 | 744 | 122 | 737.78 | 6.22 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 99.16 | 0 | 100 | 62.7 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W07 | 2023-06-06 | 49794.6 | 720 | 122 | 670.35 | 49.65 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 93.1 | 0 | 100 | 56.69 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W07 | 2023-07-07 | 50713.8 | 744 | 122 | 684.98 | 59.02 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 92.07 | 0 | 100 | 55.87 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W07 | 2022-08-08 | 57251 | 744 | 122 | 730.97 | 13.03 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 98.25 | 0 | 100 | 63.07 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W07 | 2022-09-09 | 42548.3 | 720 | 122 | 599.78 | 120.22 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 83.3 | 0 | 100 | 48.44 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W07 | 2022-10-10 | 37768.4 | 744 | 122 | 535.99 | 174.68 | 710.67 | 86701.74 | 0 | 33.33 | 0 | 0 | 33.33 | 0 | 72.04 | 0 | 95.52 | 41.61 | 0 | 28 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W07 | 2022-11-11 | 46806.4 | 720 | 122 | 619.83 | 89.87 | 709.7 | 86583.4 | 0 | 10.3 | 0 | 0 | 10.3 | 0 | 86.09 | 0 | 98.57 | 53.29 | 0 | 16 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W07 | 2022-12-12 | 42442 | 744 | 122 | 600.58 | 143.42 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 80.72 | 0 | 100 | 46.76 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W07 | Total | 510639.1 | 8760 | 122 | 6903.79 | 1802.7 | 8706.49 | 1062191.78 | 0 | 43.63 | 0 | 9.88 | 53.51 | 9.88 | 78.7817 | 0 | 99.3967 | 47.7608 | 0.0011066 | 344 | 0 | 2 | 0 | 0 | 1 | 0 | 0
W08 | 2023-01-01 | 47525.9 | 744 | 122 | 638.72 | 105.28 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 85.85 | 0 | 100 | 52.36 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W08 | 2023-02-02 | 44240.3 | 672 | 122 | 590.4 | 81.6 | 672 | 81984 | 0 | 0 | 0 | 0 | 0 | 0 | 87.86 | 0 | 100 | 53.96 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W08 | 2023-03-03 | 34134.6 | 744 | 122 | 467.25 | 266.87 | 734.12 | 89562.64 | 0 | 0 | 0 | 9.88 | 9.88 | 9.88 | 62.8 | 0 | 98.67 | 37.61 | 0.01328 | 58 | 0 | 0 | 0 | 0 | 1 | 0 | 0
W08 | 2023-04-04 | 36711.6 | 720 | 122 | 510.57 | 209.43 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 70.91 | 0 | 100 | 41.79 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W08 | 2023-05-05 | 57933.5 | 744 | 122 | 743.53 | 0.47 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 99.94 | 0 | 100 | 63.83 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W08 | 2023-06-06 | 52835.9 | 720 | 122 | 702.3 | 17.7 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 97.54 | 0 | 100 | 60.15 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W08 | 2023-07-07 | 54560.1 | 744 | 122 | 727.67 | 16.33 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 97.81 | 0 | 100 | 60.11 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W08 | 2022-08-08 | 58100.4 | 744 | 122 | 735.27 | 8.73 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 98.83 | 0 | 100 | 64.01 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W08 | 2022-09-09 | 35839.2 | 720 | 122 | 498.62 | 221.38 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 69.25 | 0 | 100 | 40.8 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W08 | 2022-10-10 | 34354.7 | 744 | 122 | 480.73 | 229.87 | 710.6 | 86693.2 | 0 | 33.4 | 0 | 0 | 33.4 | 0 | 64.61 | 0 | 95.51 | 37.85 | 0 | 40 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W08 | 2022-11-11 | 43977.1 | 720 | 122 | 578.28 | 98.57 | 676.85 | 82575.7 | 0 | 10.3 | 0 | 32.85 | 43.15 | 32.85 | 80.32 | 0 | 94.01 | 50.06 | 0.045625 | 25 | 0 | 1 | 0 | 0 | 1 | 0 | 0
W08 | 2022-12-12 | 44862.6 | 744 | 122 | 628.38 | 115.62 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 84.46 | 0 | 100 | 49.43 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W08 | Total | 545075.9 | 8760 | 122 | 7301.72 | 1371.85 | 8673.57 | 1058175.54 | 0 | 43.7 | 0 | 42.73 | 86.43 | 42.73 | 83.3483 | 0 | 99.0158 | 50.9967 | 0.0049087 | 302 | 0 | 2 | 0 | 0 | 2 | 0 | 0
W09 | 2023-01-01 | 46742.2 | 744 | 122 | 633.07 | 110.93 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 85.09 | 0 | 100 | 51.5 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W09 | 2023-02-02 | 44138.3 | 672 | 122 | 596.12 | 75.88 | 672 | 81984 | 0 | 0 | 0 | 0 | 0 | 0 | 88.71 | 0 | 100 | 53.84 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W09 | 2023-03-03 | 34532.7 | 744 | 122 | 481 | 263 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 64.65 | 0 | 100 | 38.05 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W09 | 2023-04-04 | 42227.6 | 720 | 122 | 588.58 | 126.77 | 715.35 | 87272.7 | 0 | 0 | 0.68 | 3.97 | 4.65 | 3.97 | 81.75 | 0 | 99.35 | 48.07 | 0.0055139 | 24 | 0 | 0 | 0 | 0 | 1 | 0.68 | 1
W09 | 2023-05-05 | 57419.7 | 744 | 122 | 744 | 0 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 63.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W09 | 2023-06-06 | 53416.6 | 720 | 122 | 715.68 | 4.32 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 99.4 | 0 | 100 | 60.81 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W09 | 2023-07-07 | 55404.5 | 744 | 122 | 744 | 0 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 61.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W09 | 2022-08-08 | 58074.1 | 744 | 122 | 742.7 | 1.3 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 99.83 | 0 | 100 | 63.98 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W09 | 2022-09-09 | 40881.2 | 720 | 122 | 574.52 | 145.48 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 79.79 | 0 | 100 | 46.54 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W09 | 2022-10-10 | 34945.3 | 744 | 122 | 497.08 | 210.78 | 707.86 | 86358.92 | 2.27 | 33.87 | 0 | 0 | 36.14 | 2.27 | 66.81 | 0.31 | 95.14 | 38.5 | 0.0030511 | 55 | 1 | 1 | 0 | 0 | 0 | 0 | 0
W09 | 2022-11-11 | 47426.4 | 720 | 122 | 627.3 | 81.83 | 709.13 | 86513.86 | 0 | 10.87 | 0 | 0 | 10.87 | 0 | 87.13 | 0 | 98.49 | 53.99 | 0 | 21 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W09 | 2022-12-12 | 43853.3 | 744 | 122 | 618.95 | 125.05 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 83.19 | 0 | 100 | 48.31 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W09 | Total | 559061.9 | 8760 | 122 | 7563 | 1145.34 | 8708.34 | 1062417.48 | 2.27 | 44.74 | 0.68 | 3.97 | 51.66 | 6.24 | 86.3625 | 0.025833 | 99.415 | 52.3242 | 0.00071375 | 265 | 1 | 2 | 0 | 0 | 1 | 0.68 | 1
W10 | 2023-01-01 | 47749.4 | 744 | 122 | 644.73 | 99.27 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 86.66 | 0 | 100 | 52.61 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W10 | 2023-02-02 | 42737.5 | 672 | 122 | 574.23 | 97.77 | 672 | 81984 | 0 | 0 | 0 | 0 | 0 | 0 | 85.45 | 0 | 100 | 52.13 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W10 | 2023-03-03 | 30797.4 | 744 | 122 | 426.5 | 316.65 | 743.15 | 90664.3 | 0.85 | 0 | 0 | 0 | 0.85 | 0.85 | 57.33 | 0.11 | 99.89 | 33.93 | 0.0011425 | 39 | 1 | 0 | 0 | 0 | 0 | 0 | 0
W10 | 2023-04-04 | 28432 | 720 | 122 | 388.55 | 106.72 | 495.27 | 60422.94 | 0 | 224.73 | 0 | 0 | 224.73 | 0 | 53.97 | 0 | 68.79 | 32.37 | 0 | 6 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W10 | 2023-05-05 | 57430.8 | 744 | 122 | 744 | 0 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 63.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W10 | 2023-06-06 | 53900.3 | 720 | 122 | 720 | 0 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 61.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W10 | 2023-07-07 | 55517 | 744 | 122 | 744 | 0 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 61.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W10 | 2022-08-08 | 58287 | 744 | 122 | 744 | 0 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 64.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W10 | 2022-09-09 | 39439.8 | 720 | 122 | 555.8 | 164.2 | 720 | 87840 | 0 | 0 | 0 | 0 | 0 | 0 | 77.19 | 0 | 100 | 44.9 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W10 | 2022-10-10 | 30353.3 | 744 | 122 | 427.91 | 282.12 | 710.03 | 86623.66 | 0 | 33.97 | 0 | 0 | 33.97 | 0 | 57.51 | 0 | 95.43 | 33.44 | 0 | 57 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W10 | 2022-11-11 | 45505.5 | 720 | 122 | 598.45 | 110.68 | 709.13 | 86513.86 | 0 | 10.87 | 0 | 0 | 10.87 | 0 | 83.12 | 0 | 98.49 | 51.81 | 0 | 21 | 0 | 1 | 0 | 0 | 0 | 0 | 0
W10 | 2022-12-12 | 44916.2 | 744 | 122 | 630.83 | 113.17 | 744 | 90768 | 0 | 0 | 0 | 0 | 0 | 0 | 84.79 | 0 | 100 | 49.48 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0
W10 | Total | 535066.2 | 8760 | 122 | 7199 | 1290.58 | 8489.58 | 1035728.76 | 0.85 | 269.57 | 0 | 0 | 270.42 | 0.85 | 82.1683 | 0.0091667 | 96.8833 | 50.0567 | 9.5206e-05 | 240 | 1 | 3 | 0 | 0 | 0 | 0 | 0
WAN | TOTAL | 4426030.6 | 87600 |  | 59762.46 | 22531.14 | 82293.6 | 10039819.2 | 57.22 | 5170.44 | 2.08 | 76.66 | 5306.4 | 133.88 | 68.1843 | 0.064333 | 93.9045 | 41.3892 | 0.0015171 | 2865 | 4 | 26 | 1.15 | 1 | 11 | 0.93 | 2
Total Project |  | 8526156.8 | [9 empty] | FOF: 0.085375; AF: 89.9254
PR Availability Factor by Month |  |  |  | PR Forced Outage Factor |  |  | Percentage | YTD Percentage | FOER Hours | Accumulated Hours | Total Hours | YTD hours |  | PR | MWH per month | Available MWH |  | PR | Reserve Shutdown
| Actual | Required |  |  | Actual | Goal < 0.40
Jan | 89.352 | 88.16% |  | Jan | 0 | 0.4 | 0 | 0 | 0 | 7440 | 7440 | 0 |  | Jan | 376751.2 | 631537.2 |  | Jan | 131
Feb | 88.932 | 86.88% |  | Feb | 0.944 | 0.4 | 0.94345 | 0.44774 | 63.4 | 14160 | 6720 | 63.4 |  | Feb | 353872.6 | 567742.8 |  | Feb | 142
Mar | 87.54 | 83.33% |  | Mar | 0 | 0.4 | 0 | 0.29352 | 0 | 21600 | 7440 | 63.4 |  | Mar | 293795 | 618720.75 |  | Mar | 129
Apr | 89.479 | 86.49% |  | Apr | 0 | 0.4 | 0 | 0.22014 | 0 | 28800 | 7200 | 63.4 |  | Apr | 228391.4 | 612037.5 |  | Apr | 22
May | 89.805 | 89.6% |  | May | 0 | 0.4 | 0 | 0.17494 | 0 | 36240 | 7440 | 63.4 |  | May | 443110.1 | 634736.8 |  | May | 62
Jun | 89.948 | 89.6% |  | Jun | 0.052 | 0.4 | 0.051667 | 0.15451 | 3.72 | 43440 | 7200 | 67.12 |  | Jun | 326911.8 | 615246.6 |  | Jun | 102
Jul | 90 | 89.6% |  | Jul | 0 | 0.4 | 0 | 0.13192 | 0 | 50880 | 7440 | 67.12 |  | Jul | 323022.1 | 636120 |  | Jul | 144
Aug | 90 | 88.4% |  | Aug | 0 | 0.4 | 0 | 0.11509 | 0 | 58320 | 7440 | 67.12 |  | Aug | 453088.7 | 636120 |  | Aug | 98
Sep | 80.571 | 64.2% |  | Sep | 0 | 0.4 | 0 | 0.10244 | 0 | 65520 | 7200 | 67.12 |  | Sep | 301940.6 | 551099.75 |  | Sep | 200
Oct | 71.659 | 62.2% |  | Oct | 0 | 0.4 | 0 | 0.091996 | 0 | 72960 | 7440 | 67.12 |  | Oct | 251569.1 | 506483.95 |  | Oct | 160
Nov | 79.114 | 60.8% |  | Nov | 0.281 | 0.4 | 0.28042 | 0.10892 | 20.19 | 80160 | 7200 | 87.31 |  | Nov | 336625.2 | 541138.05 |  | Nov | 174
Dec | 84.956 | 85.5% |  | Dec | 0 | 0.4 | 0 | 0.099669 | 0 | 87600 | 7440 | 87.31 |  | Dec | 411048.4 | 600471.25 |  | Dec | 89
Wan Availability Factor by Month |  |  |  | Wan Forced Outage Factor |  |  |  | YTD Percentage | FOER Hours | Accumulated Hours | Total Hours | YTD hours |  | Wan | MWH per month | Available MWH |  | Wan | Reserve Shutdown
| Actual | Required |  |  | Actual | Goal < 0.40 | Percentage
Jan | 87.743 | 85.84% |  | Jan | 0 | 0.4 | 0 | 0 | 0 | 7440 | 7440 | 0 |  | Jan | 388831.3 | 796422.1 |  | Jan | 221
Feb | 90 | 87.12% |  | Feb | 0 | 0.4 | 0 | 0 | 0 | 14160 | 6720 | 0 |  | Feb | 363089.8 | 737856 |  | Feb | 239
Mar | 92.067 | 86.67% |  | Mar | 0.011 | 0.4 | 0.011425 | 0.0039352 | 0.85 | 21600 | 7440 | 0.85 |  | Mar | 276667.9 | 835673.16 |  | Mar | 441
Apr | 95.642 | 89.51% |  | Apr | 0 | 0.4 | 0 | 0.0029514 | 0 | 28800 | 7200 | 0.85 |  | Apr | 218059.9 | 840122.5 |  | Apr | 210
May | 99.92 | 99.6% |  | May | 0 | 0.4 | 0 | 0.0023455 | 0 | 36240 | 7440 | 0.85 |  | May | 529890 | 906961.42 |  | May | 125
Jun | 99.913 | 99.6% |  | Jun | 0.087 | 0.4 | 0.086806 | 0.016344 | 6.25 | 43440 | 7200 | 7.1 |  | Jun | 352305.7 | 877637.5 |  | Jun | 334
Jul | 100 | 99.6% |  | Jul | 0 | 0.4 | 0 | 0.013954 | 0 | 50880 | 7440 | 7.1 |  | Jul | 364392.6 | 907680 |  | Jul | 330
Aug | 99.109 | 97.6% |  | Aug | 0 | 0.4 | 0 | 0.012174 | 0 | 58320 | 7440 | 7.1 |  | Aug | 519651.4 | 899593.84 |  | Aug | 135
Sep | 86.512 | 65.8% |  | Sep | 0 | 0.4 | 0 | 0.010836 | 0 | 65520 | 7200 | 7.1 |  | Sep | 318085.4 | 759919.7 |  | Sep | 157
Oct | 84.542 | 67.8% |  | Oct | 0.674 | 0.4 | 0.67366 | 0.078427 | 50.12 | 72960 | 7440 | 57.22 |  | Oct | 259401.6 | 767383.66 |  | Oct | 289
Nov | 91.486 | 69.2% |  | Nov | 0 | 0.4 | 0 | 0.071382 | 0 | 80160 | 7200 | 57.22 |  | Nov | 408087 | 803612.78 |  | Nov | 182
Dec | 99.92 | 98.1% |  | Dec | 0 | 0.4 | 0 | 0.06532 | 0 | 87600 | 7440 | 57.22 |  | Dec | 427568 | 906956.54 |  | Dec | 202
Project Availability Factor by Month |  |  |  | Project Forced Outage Factor |  |  |  | YTD Percentage | FOER Hours | Accumulated Hours | Total Hours | MOH: YTD hours; UOH: Project; SF: MWH per month; FOF: Available MWH
| Actual | Required |  |  | Actual | Goal < 0.40 | Percentage
Jan | 88.5475 | 87 |  | Jan | 0 | 0.4 | 0 | 0 | 0 | 14880 | 14880 | MOH: 0; UOH: Jan; SF: 765582.5; FOF: 1427959.3
Feb | 89.466 | 87 |  | Feb | 0.472 | 0.4 | 0.47173 | 0.22387 | 63.4 | 28320 | 13440 | MOH: 63.4; UOH: Feb; SF: 716962.4; FOF: 1305598.8
Mar | 89.8035 | 85 |  | Mar | 0.0055 | 0.4 | 0.0057124 | 0.14873 | 0.85 | 43200 | 14880 | MOH: 64.25; UOH: Mar; SF: 570462.9; FOF: 1454393.91
Apr | 92.5605 | 88 |  | Apr | 0 | 0.4 | 0 | 0.11155 | 0 | 57600 | 14400 | MOH: 64.25; UOH: Apr; SF: 446451.3; FOF: 1452160
May | 94.8625 | 94.6 |  | May | 0 | 0.4 | 0 | 0.088645 | 0 | 72480 | 14880 | MOH: 64.25; UOH: May; SF: 973000.1; FOF: 1541698.22
Jun | 94.9305 | 94.6 |  | Jun | 0.0695 | 0.4 | 0.069236 | 0.085428 | 9.97 | 86880 | 14400 | MOH: 74.22; UOH: Jun; SF: 679217.5; FOF: 1492884.1
Jul | 95 | 94.6 |  | Jul | 0 | 0.4 | 0 | 0.072936 | 0 | 101760 | 14880 | MOH: 74.22; UOH: Jul; SF: 687414.7; FOF: 1543800
Aug | 94.5545 | 93 |  | Aug | 0 | 0.4 | 0 | 0.063632 | 0 | 116640 | 14880 | MOH: 74.22; UOH: Aug; SF: 972740.1; FOF: 1535713.84
Sep | 83.5415 | 65 |  | Sep | 0 | 0.4 | 0 | 0.056639 | 0 | 131040 | 14400 | MOH: 74.22; UOH: Sep; SF: 620026; FOF: 1311019.45
Oct | 78.1005 | 65 |  | Oct | 0.337 | 0.4 | 0.33683 | 0.085211 | 50.12 | 145920 | 14880 | MOH: 124.34; UOH: Oct; SF: 510970.7; FOF: 1273867.61
Nov | 85.3 | 65 |  | Nov | 0.1405 | 0.4 | 0.14021 | 0.090151 | 20.19 | 160320 | 14400 | MOH: 144.53; UOH: Nov; SF: 744712.2; FOF: 1344750.83
Dec | 92.438 | 91.8 |  | Dec | 0 | 0.4 | 0 | 0.082494 | 0 | 175200 | 14880 | MOH: 144.53; UOH: Dec; SF: 838616.4; FOF: 1507427.79

## Sheet1
HOURS | JAN | FEB | MAR | APR | MAY | JUN | JUL | AUG | SEP | OCT | NOV | DEC
REMAINING | 65.2 | 127.4 | 150.8 | -392 | 34 | 258 | 45.52 | 200.6 | 2310 | 1772 | 2670 | 242.16